## Sheet1
|  | Name: Amritanshu Raj | Follow me: | amritanshu19 (Amritanshu Raj) · GitHub
https://www.linkedin.com/in/amritanshu-raj-42311a168/
Population and water requirements |  |  |  | Amritanshu Raj (@amritanshu1937) / Twitter
Current population | 101005
Design period (in Yrs) | 15 |  |  | Design as per Indian Standards.
Design population growth | Geometric
Pn | 112578.5289 | 112579
Water required |  | Per capita demand (lpcd) | Net Total
Water required = poplulation * per capita | 112579 | 135 | 15198165
|  | Total water needed (litres/day) | 15198165
|  | Assume 20% loss | 18237798
|  | in (MLD) | 18.2378
|  | in (m^3/s) | 0.21109
|  | in (m^3/h) | 759.9082
Aeratation unit
Q (m^3/h) | 759.9082
Type: diffuse aerators
Dimensions of aerator tanks | L = 10m | B = 8m | H = 5m
Area (m^2) | 80
Volume (m^3) | 400
No. of tanks | 2
No. of diffusers each tank | 80
Total diffusers required | 160
Radius of a diffuser (m) | 0.2
Coagulation
Rapid mix unit design
Q (m^3/h) | 759.9082
Mixing time (min) | 2
Volume of mixing basin (m^3) | 25.3303
Cubical mixing basin (a) | 2.9368
Assume a to be (m) | 3
Provided volume of basin | 27
T (deg C) | 20
µ (N.s/m2) | 0.0010016
G (/s) | 800
Power required (Kw) | 17.3076
Monthly Alum Requirement
Q (m^3/h) | 759.9082
Q (m^3/month) | 547133.94
Opitmal alum dose (mg/l) | 20
Opitmal alum dose (kg/m^3) | 0.02
Alum required (kg/month) | 10942.6788
Sedimentation
Shape: Rectangular
Q (m^3/h) | 759.9082
No. of tanks | 4
Volume of each tank | 189.9771
Settling velocity
Maximum size of the particle, d (mm) | 0.02
Expected removal efficiency (%) | 75
Specific gravity G | 2.65
Assumed performance of tank, good (n) | 0.25
Dynamic viscosity µ (N.s/m^2) (T = 20C) | 0.0010016
Kinematic viscosity (m^2 /s) | 1.0016e-06
g (m^2/s) | 9.81
Vertical settling velocity (m/s) | 0.00035913
Reynolds’s number (Re) | 0.007171
Surface overflow rate
Vs (m/s) | 0.00035913
Vo = Vs (m/day) | 20.6856
n | 0.25
Y/Yo | 0.75
Vo/(Q/A) | 1.657
Q/A | 12.4838
Dimensions of tank
Q (m^3/s) | 189.9771
Surface area of tank (A) | 365.2299
Length:width | 3:1
Width | 11.0337
Length | 33.1012
Assuming a detention period (hours) | 4
Depth of tank | 2.0806
resuspension of deposited particles
β (uni granular sand) | 0.04
f’ (Darcy Weisbach friction factor) | 0.03
G | 2.65
d (m) | 2e-05
g (m/s^2) | 9.81
Scour velocity (Vd) (m/s) | 0.058763
Q (m^3/s) | 189.9771
Width | 11.0337
Depth of tank | 2.0806
Horizontal velocity (Vh) | 0.0022987
FLOCCULATION
Assumption GT | 45000
G1 (/s) | 50
G2 (/s) | 40
G3 (/s) | 30
G4 (/s) | 20
G5 (/s) | 10
Average G (/s) | 30
Average detention Time (T) (min) | 25
Q (m^3/h) | 759.9082
Q (m^3/day) | 18237.798
Q (m^3/min) | 12.6651
volume (m^3) | 316.6284
assume depth of the tank (m) | 5
Area (m^2) | 63.3257
total number of compartments | 10
Area of compartment (m^2) | 6.3326
Assume the length of one stage (m) | 3
Width | 2.1109
Power in each Compartment
volume (m^3) | 316.6284
volume of each stage (m^3) | 63.3257
G1 (/s) | 50
G2 (/s) | 40
G3 (/s) | 30
G4 (/s) | 20
G5 (/s) | 10
μ (N.s/m^2) | 0.0010016
Power in each Compartment
P1 (watt) | 158.5675
P2 (watt) | 101.4832
P3 (watt) | 57.0843
P4 (watt) | 25.3708
P5 (watt) | 6.3427
Paddle Design
For first compartment
P1 (watt) | 158.5675
Cd (flat blades) | 1.8
Density (kg/m^3) | 1000
Actual speed of paddle (assume) Vp`(m/s) | 0.67
Vp (m/s) | 0.5025
Assume width of padle be 'w'
Area of paddle (Ap) in w terms (m^2) | 31.2w
Ap (m^2) | 1.3886
w (m) | 0.044505
Ap (m^2) | 1.3886
w (rev/s) | 0.06668
w (rev/min) | 4.0008
For Second compartment
P2 (watt) | 101.4832
Vp (m/s) | 0.027069
Vp actual (m/s) | 0.036092
w (rev/s) | 0.0047892
w (rev/min) | 0.28735
For Third compartment
P3 (watt) | 57.0843
Vp (m/s) | 0.015226
Vp actual (m/s) | 0.020302
w (rev/s) | 0.0026939
w (rev/min) | 0.16164
For Fourth compartment
P4 (watt) | 25.3708
Vp (m/s) | 0.0067672
Vp actual (m/s) | 0.0090229
w (rev/s) | 0.0011973
w (rev/min) | 0.071838
For Fifth compartment
P5 (watt) | 6.3427
Vp (m/s) | 0.0016918
Vp actual (m/s) | 0.0022557
w (rev/s) | 0.00029933
w (rev/min) | 0.01796
Clarifier
Designed to be same as sedimentation tank
Filtration
Type: Rapid sand Filter
Q (MLD) | 18.2378
Q (m^3/hr) | 759.9082
Number of tanks | 4
Q (each tank) (m^3/hr) | 189.9771
Back wash requirement (5% of Q) (m^3/hr) | 9.4989
Net Q(m^3/hr) | 199.4759
Q adjusted for backwashing time loss | 208.1488
Va (filtering velocity) (m/hr) | 5
Area of each tank (m^2) | 41.6298
Assume L/B | 1.25
B | 5.7709
L | 7.2137
Frictional Head Loss :
μ (N.s/m2) | 0.0010016
Filter Medium (Sand) depth (m) | 0.67
Filtering Velocity Va (m/hr) | 5
Va (m/s) | 0.0013889
Depth of particles dp (mm) | 0.6
Specific Gravity G | 2.65
Porosity e | 0.4
Shape factor ψ | 0.85
Re (Reynolds number) | 0.7072
f' | 129.0121
Hf (m) | 0.26558
Hf (mm) | 265.5775
Design of under drainage system
Plan area (m^2) | 41.6298
L (m) | 7.2137
B (m) | 5.7709
total area of perforations(m^2) | 0.20815
total area of perforations(cm^2) | 2081.4878
Total cross-sectional area of laterals (cm^2) | 6244.4634
Area of manifold (cm^2) | 12488.9269
Diameter of central manifold (cm) | 126.1327
Number of laterals | 98
cross sectional area of one lateral(cm^2) | 31.8595
Diameter of lateral(cm) | 6.3707
Length of lateral(m) | 2.2548
Design of back water trough
Plan area (m^2) | 41.6298
rate of washing of the filter (m/min) | 0.6
Wash water discharge (m^3/hr) | 1498.6712
Wash water discharge (m^3/sec) | 0.4163
Assume wash water trough spacing (m) | 1.6
Number of trough | 3.6068
Discharge per unit trough (m^3/sec) | 0.10407
assume wash water trough width (m) | 0.4
height of each trough | 0.32944
DISINFECTION
Assuming Chlorine Dosage (mg/L) | 0.3
Chlorine Dosage (kg/m^3) | 0.0003
Q (m^3/day) | 18237.798
Total chlorine required (kg/day) | 5.4713
The end